## SettingParam.run (Tar)
No. | Equip ID | Sig Type | Sig ID | Signal Key | Parameter Name | Category / Section | Value Type | Tar Value (Raw) | Tar Value (Interpreted) | Live Value SE (10.209.57.21) | Live Value BAT (10.209.1.21) | Tar Timestamp (Epoch) | Tar Timestamp (Datetime) | Options / Units
1 | 1 | 2 | 7 | 1:2:7 | Auto/Manual State | UDEF_SET_4.list | 5 | 0 | 0 (Auto) | 0 | 0 | 1790821825 | 2026-10-01 09:30:25 | [['Auto', '自动'], ['Manual', '手动']]
2 | 1 | 2 | 24 | 1:2:24 | Unknown Signal [1:24] | - | 2 | 1192198327 | 36736.71 | - | - | 1791073438 | 2026-10-04 07:23:58
3 | 1 | 2 | 11 | 1:2:11 | Maintenance Cycle Time | UDEF_SET_1.list | 3 | 7200 | 7200 | 7200 | 7200 | 1690547498 | 2023-07-28 19:31:38 | d
4 | 1 | 2 | 22 | 1:2:22 | Unknown Signal [1:22] | - | 3 | 0 | 0 | - | - | 1779331763 | 2026-05-21 09:49:23
5 | 1 | 2 | 448 | 1:2:448 | Timezone Offset (Seconds) | System Time | 3 | -25200 | -25200 s (UTC+7) | - | - | 1707209730 | 2024-02-06 15:55:30
6 | 1 | 2 | 23 | 1:2:23 | Unknown Signal [1:23] | - | 3 | 1 | 1 | - | - | 1625497371 | 2021-07-05 22:02:51
7 | 1 | 2 | 35 | 1:2:35 | Unknown Signal [1:35] | - | 3 | 1 | 1 | - | - | 1625497345 | 2021-07-05 22:02:25
8 | 1 | 2 | 8 | 1:2:8 | Outgoing Alarms Blocked | WIZARD.list | 5 | 0 | 0 (Normal) | 0 | 0 | 1779331457 | 2026-05-21 09:44:17 | [['Normal', '正常'], ['Blocked', '阻塞']]
9 | 1 | 2 | 26 | 1:2:26 | Unknown Signal [1:26] | - | 3 | 436064522 | 436064522 | - | - | 1707209730 | 2024-02-06 15:55:30
10 | 1 | 2 | 27 | 1:2:27 | Unknown Signal [1:27] | - | 3 | 435998986 | 435998986 | - | - | 1707209730 | 2024-02-06 15:55:30
11 | 1 | 2 | 28 | 1:2:28 | NTP Sync Interval | System Time | 3 | 60 | 60 min | - | - | 1707209730 | 2024-02-06 15:55:30
12 | 1 | 2 | 183 | 1:2:183 | Unknown Signal [1:183] | - | 3 | 0 | 0 | - | - | 1199145637 | 2008-01-01 07:00:37
13 | 1 | 2 | 189 | 1:2:189 | Under Voltage 1 | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 2 | 1111490560 | 48.0 V | 48.0 | 48.0 | 1625528334 | 2021-07-06 06:38:54 | V
14 | 1 | 2 | 190 | 1:2:190 | Under Voltage 2 | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 2 | 1110966272 | 46.0 V | 46.0 | 46.0 | 1625528347 | 2021-07-06 06:39:07 | V
15 | 1 | 2 | 208 | 1:2:208 | Ambient Temp Sensor | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 5 | 3 | 3 (System Temp1) | 3 | 3 | 1199146401 | 2008-01-01 07:13:21 | [['None', '无'], ['Maximum', '最大温度'], ['Average', '平均温度'], ['System Temp1', '系统温度1'], ['System Temp2', '系统温度2'], ['System Temp3', '系统温度3'], ['IB2 Temp1', 'IB2温度1'], ['IB2 Temp2', 'IB2温度2'], ['EIB Temp1', 'EIB温度1'], ['EIB Temp2', 'EIB温度2'], ['SMTemp1 Temp1', 'SMTemp1温度1'], ['SMTemp1 Temp2', 'SMTemp1温度2'], ['SMTemp1 Temp3', 'SMTemp1温度3'], ['SMTemp1 Temp4', 'SMTemp1温度4'], ['SMTemp1 Temp5', 'SMTemp1温度5'], ['SMTemp1 Temp6', 'SMTemp1温度6'], ['SMTemp1 Temp7', 'SMTemp1温度7'], ['SMTemp1 Temp8', 'SMTemp1温度8'], ['SMTemp2 Temp1', 'SMTemp2温度1'], ['SMTemp2 Temp2', 'SMTemp2温度2'], ['SMTemp2 Temp3', 'SMTemp2温度3'], ['SMTemp2 Temp4', 'SMTemp2温度4'], ['SMTemp2 Temp5', 'SMTemp2温度5'], ['SMTemp2 Temp6', 'SMTemp2温度6'], ['SMTemp2 Temp7', 'SMTemp2温度7'], ['SMTemp2 Temp8', 'SMTemp2温度8'], ['SMTemp3 Temp1', 'SMTemp3温度1'], ['SMTemp3 Temp2', 'SMTemp3温度2'], ['SMTemp3 Temp3', 'SMTemp3温度3'], ['SMTemp3 Temp4', 'SMTemp3温度4'], ['SMTemp3 Temp5', 'SMTemp3温度5'], ['SMTemp3 Temp6', 'SMTemp3温度6'], ['SMTemp3 Temp7', 'SMTemp3温度7'], ['SMTemp3 Temp8', 'SMTemp3温度8'], ['SMTemp4 Temp1', 'SMTemp4温度1'], ['SMTemp4 Temp2', 'SMTemp4温度2'], ['SMTemp4 Temp3', 'SMTemp4温度3'], ['SMTemp4 Temp4', 'SMTemp4温度4'], ['SMTemp4 Temp5', 'SMTemp4温度5'], ['SMTemp4 Temp6', 'SMTemp4温度6'], ['SMTemp4 Temp7', 'SMTemp4温度7'], ['SMTemp4 Temp8', 'SMTemp4温度8'], ['SMTemp5 Temp1', 'SMTemp5温度1'], ['SMTemp5 Temp2', 'SMTemp5温度2'], ['SMTemp5 Temp3', 'SMTemp5温度3'], ['SMTemp5 Temp4', 'SMTemp5温度4'], ['SMTemp5 Temp5', 'SMTemp5温度5'], ['SMTemp5 Temp6', 'SMTemp5温度6'], ['SMTemp5 Temp7', 'SMTemp5温度7'], ['SMTemp5 Temp8', 'SMTemp5温度8'], ['SMTemp6 Temp1', 'SMTemp6温度1'], ['SMTemp6 Temp2', 'SMTemp6温度2'], ['SMTemp6 Temp3', 'SMTemp6温度3'], ['SMTemp6 Temp4', 'SMTemp6温度4'], ['SMTemp6 Temp5', 'SMTemp6温度5'], ['SMTemp6 Temp6', 'SMTemp6温度6'], ['SMTemp6 Temp7', 'SMTemp6温度7'], ['SMTemp6 Temp8', 'SMTemp6温度8'], ['SMTemp7 Temp1', 'SMTemp7温度1'], ['SMTemp7 Temp2', 'SMTemp7温度2'], ['SMTemp7 Temp3', 'SMTemp7温度3'], ['SMTemp7 Temp4', 'SMTemp7温度4'], ['SMTemp7 Temp5', 'SMTemp7温度5'], ['SMTemp7 Temp6', 'SMTemp7温度6'], ['SMTemp7 Temp7', 'SMTemp7温度7'], ['SMTemp7 Temp8', 'SMTemp7温度8'], ['SMTemp8 Temp1', 'SMTemp8温度1'], ['SMTemp8 Temp2', 'SMTemp8温度2'], ['SMTemp8 Temp3', 'SMTemp8温度3'], ['SMTemp8 Temp4', 'SMTemp8温度4'], ['SMTemp8 Temp5', 'SMTemp8温度5'], ['SMTemp8 Temp6', 'SMTemp8温度6'], ['SMTemp8 Temp7', 'SMTemp8温度7'], ['SMTemp8 Temp8', 'SMTemp8温度8']]
16 | 1 | 2 | 209 | 1:2:209 | Ambient Temp High1 | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 2 | 1108869120 | 38.0 deg.C | 38 | 38 | 1625529688 | 2021-07-06 07:01:28 | deg.C
17 | 1 | 2 | 210 | 1:2:210 | Ambient Temp Low | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 2 | 1097859072 | 15.0 deg.C | 15 | 15 | 1635346375 | 2021-10-27 21:52:55 | deg.C
18 | 1 | 2 | 50 | 1:2:50 | System Temp 1 | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 5 | 1 | 1 (Ambient) | 1 | 1 | 1617281740 | 2021-04-01 19:55:40 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']]
19 | 1 | 2 | 51 | 1:2:51 | System Temp 2 | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | 5 | 2 | 2 (Battery) | 2 | 2 | 1617281747 | 2021-04-01 19:55:47 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']]
20 | 1 | 2 | 457 | 1:2:457 | Unknown Signal [1:457] | - | 3 | 1 | 1 | - | - | 1199145947 | 2008-01-01 07:05:47
21 | 1 | 2 | 701 | 1:2:701 | Unknown Signal [1:701] | - | 3 | 1 | 1 | - | - | 1707209730 | 2024-02-06 15:55:30
22 | 2 | 2 | 30 | 2:2:30 | Restart on HVSD | RECT.list | 5 | 1 | 1 (Enabled) | 1 | 1 | 1779331462 | 2026-05-21 09:44:22 | [['Disabled', '否'], ['Enabled', '是']]
23 | 2 | 2 | 6 | 2:2:6 | HVSD Restart Time | RECT.list | 3 | 300 | 300 | 300 | 300 | 1779331462 | 2026-05-21 09:44:22 | s
24 | 2 | 2 | 31 | 2:2:31 | Sequence Start Interval | RECT.list | 3 | 0 | 0 | 0 | 0 | 1779331462 | 2026-05-21 09:44:22 | s
25 | 2 | 2 | 8 | 2:2:8 | Walk-In | RECT.list | 5 | 1 | 1 (Enabled) | 1 | 1 | 1779331462 | 2026-05-21 09:44:22 | [['Disabled', '否'], ['Enabled', '是']]
26 | 2 | 2 | 7 | 2:2:7 | Walk-In Time | RECT.list | 3 | 8 | 8 | 8 | 8 | 1779331462 | 2026-05-21 09:44:22 | s
27 | 2 | 2 | 18 | 2:2:18 | Rectifier Number in Group | Rectifier System | 3 | 2 | 2 units | - | - | 1199148202 | 2008-01-01 07:43:22
28 | 2 | 2 | 19 | 2:2:19 | Turn On when AC Over Voltage | RECT.list | 5 | 0 | 0 (Yes) | 0 | 0 | 1779331462 | 2026-05-21 09:44:22 | [['Yes', '是'], ['No', '否']]
29 | 3 | 2 | 1 | 3:2:1 | Rectifier #1 Phase | Rectifier Phase | 3 | 1 | Phase A (1) | - | - | 1789033252 | 2026-09-10 16:40:52
30 | 3 | 2 | 2 | 3:2:2 | Unknown Signal [3:2] | - | 3 | 0 | 0 | - | - | 1789033252 | 2026-09-10 16:40:52
31 | 4 | 2 | 1 | 4:2:1 | Rectifier #2 Phase | Rectifier Phase | 3 | 2 | Phase B (2) | - | - | 1789033252 | 2026-09-10 16:40:52
32 | 4 | 2 | 2 | 4:2:2 | Unknown Signal [4:2] | - | 3 | 0 | 0 | - | - | 1789033252 | 2026-09-10 16:40:52
33 | 104 | 2 | 4 | 104:2:4 | Mains Failure Alarm Limit 1 | PowerSystem.AC_UNIT.Rectifier AC,模块交流.list | 2 | 1097859072 | 15.0 % | 15.0 | 15.0 | 1625529832 | 2021-07-06 07:03:52 | %
34 | 104 | 2 | 5 | 104:2:5 | Mains Failure Alarm Limit 2 | PowerSystem.AC_UNIT.Rectifier AC,模块交流.list | 2 | 1097859072 | 15.0 % | 15.0 | 15.0 | 1625529839 | 2021-07-06 07:03:59 | %
35 | 115 | 2 | 64 | 115:2:64 | Number of Battery Shunts | CHARGE.list | 5 | 1 | 1 (1) | 1 | 1 | 1199148185 | 2008-01-01 07:43:05 | [['0', '0'], ['1', '1'], ['2', '2']]
36 | 115 | 2 | 17 | 115:2:17 | Equalize Charge Voltage | WIZARD.list | 2 | 1112958566 | 53.6 V | 53.6 | 53.6 | 1617282413 | 2021-04-01 20:06:53 | V
37 | 115 | 2 | 21 | 115:2:21 | Automatic Equalize | CHARGE.list | 5 | 0 | 0 (No) | 0 | 0 | 1617284305 | 2021-04-01 20:38:25 | [['No', '否'], ['Yes', '是']]
38 | 115 | 2 | 24 | 115:2:24 | Cyclic Equalize | CHARGE.list | 5 | 0 | 0 (No) | 0 | 0 | 1617284322 | 2021-04-01 20:38:42 | [['No', '否'], ['Yes', '是']]
39 | 115 | 2 | 11 | 115:2:11 | AC Fail Test | BATT_TEST.list | 5 | 0 | 0 (Disabled) | 0 | 0 | 1625531622 | 2021-07-06 07:33:42 | [['Disabled', '否'], ['Enabled', '是']]
40 | 115 | 2 | 63 | 115:2:63 | Temp Compensation Probe Number | WIZARD.list | 5 | 5 | 5 (System Temp2) | 5 | 5 | 1199146251 | 2008-01-01 07:10:51 | [['None', '无'], ['Maximum', '最大温度'], ['Average', '平均温度'], ['Average SMBRC', 'SMBRC平均温度'], ['System Temp1', '系统温度1'], ['System Temp2', '系统温度2'], ['System Temp3', '系统温度3'], ['IB2 Temp1', 'IB2温度1'], ['IB2 Temp2', 'IB2温度2'], ['EIB Temp1', 'EIB温度1'], ['EIB Temp2', 'EIB温度2'], ['SMTemp1 Temp1', 'SMTemp1温度1'], ['SMTemp1 Temp2', 'SMTemp1温度2'], ['SMTemp1 Temp3', 'SMTemp1温度3'], ['SMTemp1 Temp4', 'SMTemp1温度4'], ['SMTemp1 Temp5', 'SMTemp1温度5'], ['SMTemp1 Temp6', 'SMTemp1温度6'], ['SMTemp1 Temp7', 'SMTemp1温度7'], ['SMTemp1 Temp8', 'SMTemp1温度8'], ['SMTemp2 Temp1', 'SMTemp2温度1'], ['SMTemp2 Temp2', 'SMTemp2温度2'], ['SMTemp2 Temp3', 'SMTemp2温度3'], ['SMTemp2 Temp4', 'SMTemp2温度4'], ['SMTemp2 Temp5', 'SMTemp2温度5'], ['SMTemp2 Temp6', 'SMTemp2温度6'], ['SMTemp2 Temp7', 'SMTemp2温度7'], ['SMTemp2 Temp8', 'SMTemp2温度8'], ['SMTemp3 Temp1', 'SMTemp3温度1'], ['SMTemp3 Temp2', 'SMTemp3温度2'], ['SMTemp3 Temp3', 'SMTemp3温度3'], ['SMTemp3 Temp4', 'SMTemp3温度4'], ['SMTemp3 Temp5', 'SMTemp3温度5'], ['SMTemp3 Temp6', 'SMTemp3温度6'], ['SMTemp3 Temp7', 'SMTemp3温度7'], ['SMTemp3 Temp8', 'SMTemp3温度8'], ['SMTemp4 Temp1', 'SMTemp4温度1'], ['SMTemp4 Temp2', 'SMTemp4温度2'], ['SMTemp4 Temp3', 'SMTemp4温度3'], ['SMTemp4 Temp4', 'SMTemp4温度4'], ['SMTemp4 Temp5', 'SMTemp4温度5'], ['SMTemp4 Temp6', 'SMTemp4温度6'], ['SMTemp4 Temp7', 'SMTemp4温度7'], ['SMTemp4 Temp8', 'SMTemp4温度8'], ['SMTemp5 Temp1', 'SMTemp5温度1'], ['SMTemp5 Temp2', 'SMTemp5温度2'], ['SMTemp5 Temp3', 'SMTemp5温度3'], ['SMTemp5 Temp4', 'SMTemp5温度4'], ['SMTemp5 Temp5', 'SMTemp5温度5'], ['SMTemp5 Temp6', 'SMTemp5温度6'], ['SMTemp5 Temp7', 'SMTemp5温度7'], ['SMTemp5 Temp8', 'SMTemp5温度8'], ['SMTemp6 Temp1', 'SMTemp6温度1'], ['SMTemp6 Temp2', 'SMTemp6温度2'], ['SMTemp6 Temp3', 'SMTemp6温度3'], ['SMTemp6 Temp4', 'SMTemp6温度4'], ['SMTemp6 Temp5', 'SMTemp6温度5'], ['SMTemp6 Temp6', 'SMTemp6温度6'], ['SMTemp6 Temp7', 'SMTemp6温度7'], ['SMTemp6 Temp8', 'SMTemp6温度8'], ['SMTemp7 Temp1', 'SMTemp7温度1'], ['SMTemp7 Temp2', 'SMTemp7温度2'], ['SMTemp7 Temp3', 'SMTemp7温度3'], ['SMTemp7 Temp4', 'SMTemp7温度4'], ['SMTemp7 Temp5', 'SMTemp7温度5'], ['SMTemp7 Temp6', 'SMTemp7温度6'], ['SMTemp7 Temp7', 'SMTemp7温度7'], ['SMTemp7 Temp8', 'SMTemp7温度8'], ['SMTemp8 Temp1', 'SMTemp8温度1'], ['SMTemp8 Temp2', 'SMTemp8温度2'], ['SMTemp8 Temp3', 'SMTemp8温度3'], ['SMTemp8 Temp4', 'SMTemp8温度4'], ['SMTemp8 Temp5', 'SMTemp8温度5'], ['SMTemp8 Temp6', 'SMTemp8温度6'], ['SMTemp8 Temp7', 'SMTemp8温度7'], ['SMTemp8 Temp8', 'SMTemp8温度8']]
41 | 115 | 2 | 5 | 115:2:5 | End Test Time | BATT_TEST.list | 3 | 150 | 150 | 150 | 30 | 1746713427 | 2025-05-08 21:10:27 | min
42 | 115 | 2 | 47 | 115:2:47 | Number of Planned Tests per Year | BATT_TEST.list | 3 | 12 | 12 | 12 | 12 | 1626803754 | 2021-07-21 00:55:54
43 | 115 | 2 | 48 | 115:2:48 | Planned Test 1 (MM-DD Hr) | BATT_TEST.list | 4 | 63072450 | 63072450 | 63072450 | 63072450 | 1626803771 | 2021-07-21 00:56:11
44 | 115 | 2 | 49 | 115:2:49 | Planned Test 2 (MM-DD Hr) | BATT_TEST.list | 4 | 65750850 | 65750850 | 65750850 | 65750850 | 1626803789 | 2021-07-21 00:56:29
45 | 115 | 2 | 50 | 115:2:50 | Planned Test 3 (MM-DD Hr) | BATT_TEST.list | 4 | 68256450 | 68256450 | 68256450 | 68256450 | 1626803795 | 2021-07-21 00:56:35
46 | 115 | 2 | 51 | 115:2:51 | Planned Test 4 (MM-DD Hr) | BATT_TEST.list | 4 | 70934850 | 70934850 | 70934850 | 70934850 | 1626803800 | 2021-07-21 00:56:40
47 | 115 | 2 | 52 | 115:2:52 | Planned Test 5 (MM-DD Hr) | BATT_TEST.list | 4 | 73526850 | 73526850 | 73526850 | 73526850 | 1626803805 | 2021-07-21 00:56:45
48 | 115 | 2 | 53 | 115:2:53 | Planned Test 6 (MM-DD Hr) | BATT_TEST.list | 4 | 76223250 | 76223250 | 76223250 | 76205250 | 1790996771 | 2026-10-03 10:06:11
49 | 115 | 2 | 54 | 115:2:54 | Planned Test 7 (MM-DD Hr) | BATT_TEST.list | 4 | 78797250 | 78797250 | 78797250 | 78797250 | 1626803824 | 2021-07-21 00:57:04
50 | 115 | 2 | 55 | 115:2:55 | Planned Test 8 (MM-DD Hr) | BATT_TEST.list | 4 | 81475650 | 81475650 | 81475650 | 81475650 | 1626803828 | 2021-07-21 00:57:08
51 | 115 | 2 | 56 | 115:2:56 | Planned Test 9 (MM-DD Hr) | BATT_TEST.list | 4 | 84154050 | 84154050 | 84154050 | 84154050 | 1626803833 | 2021-07-21 00:57:13
52 | 115 | 2 | 57 | 115:2:57 | Planned Test 10 (MM-DD Hr) | BATT_TEST.list | 4 | 86746050 | 86746050 | 86746050 | 86746050 | 1626803839 | 2021-07-21 00:57:19
53 | 115 | 2 | 58 | 115:2:58 | Planned Test 11 (MM-DD Hr) | BATT_TEST.list | 4 | 89424450 | 89424450 | 89424450 | 89424450 | 1626803843 | 2021-07-21 00:57:23
54 | 115 | 2 | 59 | 115:2:59 | Planned Test 12 (MM-DD Hr) | BATT_TEST.list | 4 | 92016450 | 92016450 | 92016450 | 92016450 | 1626803851 | 2021-07-21 00:57:31
55 | 115 | 2 | 417 | 115:2:417 | Unknown Signal [115:417] | - | 3 | 0 | 0 | - | - | 1779331456 | 2026-05-21 09:44:16
56 | 116 | 2 | 10 | 116:2:10 | Batt1 Rated Capacity | WIZARD.list | 2 | 1120403456 | 100.0 Ah | 100 | 100 | 1635346381 | 2021-10-27 21:53:01 | Ah
57 | 116 | 2 | 1 | 116:2:1 | Batt1 Shunt Current | CHARGE.list | 2 | 1127153664 | 175.0 A | 175.0 | 175.0 | 1199148191 | 2008-01-01 07:43:11 | A
58 | 116 | 2 | 2 | 116:2:2 | Batt1 Shunt Voltage | CHARGE.list | 2 | 1103626240 | 25.0 mV | 25.0 | 25.0 | 1199148193 | 2008-01-01 07:43:13 | mV
59 | 186 | 2 | 59 | 186:2:59 | AC Fail Required | PowerSystem.LVD_GROUP.LVD Group,LVD组.list | 5 | 1 | 1 (Enabled) | 1 | 1 | 1199148187 | 2008-01-01 07:43:07 | [['Disabled', '否'], ['Enabled', '是']]
60 | 187 | 2 | 3 | 187:2:3 | LVD 1 | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | 5 | 1 | 1 (Enabled) | 1 | 1 | 1199148190 | 2008-01-01 07:43:10 | [['Disabled', '禁止'], ['Enabled', '允许']]
61 | 187 | 2 | 1 | 187:2:1 | LVD 1 Voltage | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | 2 | 1110232269 | 43.2 V | 43.2 | 43.2 | 1617282609 | 2021-04-01 20:10:09 | V
62 | 187 | 2 | 2 | 187:2:2 | LVD 1 Reconnect Voltage | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | 2 | 1111752704 | 49.0 V | 49.0 | 49.0 | 1617282615 | 2021-04-01 20:10:15 | V
63 | 187 | 2 | 8 | 187:2:8 | LVD 2 | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | 5 | 1 | 1 (Enabled) | 1 | 1 | 1199148180 | 2008-01-01 07:43:00 | [['Disabled', '禁止'], ['Enabled', '允许']]
64 | 187 | 2 | 7 | 187:2:7 | LVD 2 Reconnect Voltage | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | 2 | 1111752704 | 49.0 V | 49.0 | 49.0 | 1617282646 | 2021-04-01 20:10:46 | V
65 | 187 | 2 | 14 | 187:2:14 | LVD Contactor Type | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | 5 | 1 | 1 (Mono-Stable) | 1 | 1 | 1199148188 | 2008-01-01 07:43:08 | [['Bistable', '双稳'], ['Mono-Stable', '单稳'], ['Mono w/Sample', '单稳带回采']]
66 | 197 | 2 | 9 | 197:2:9 | Voltage Type | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | 5 | 3 | 3 (Disabled) | 3 | 3 | 1617281806 | 2021-04-01 19:56:46 | [['48 (Block4)', '48(Block4)'], ['Mid Point', 'Mid point'], ['24 (Block2)', '24(Block2)'], ['Disabled', '不允许']]

## MainConfig.run (Alarms & Site)
No. | Timestamp | Changed Info Type | Text Type | New Value / Text | Equip ID / Type ID | Sig Type | Sig ID | Meaning / Description
1 | 2008-01-01 00:45:47 | AL | - | NA | 100 | A | 40 | Alarm Level for Equip 100 Signal 40 -> NA
2 | 2008-01-01 00:45:47 | AR | - | NA | 100 | A | 40 | Alarm Relay output mapping for Equip 100 Signal 40 -> Relay NA
3 | 2008-01-01 00:08:33 | ST | EF | BY | - | - | - | Site Name change to: BY
4 | 2008-01-01 00:08:48 | SL | EF | Bankyeekun | - | - | - | Site Location change to: Bankyeekun
5 | 2008-01-01 00:09:07 | SD | EF | SDH3 | - | - | - | Site Description change to: SDH3
6 | 2021-04-01 12:57:31 | SD | EF | BY | - | - | - | Site Description change to: BY
7 | 2021-04-01 12:58:18 | AL | - | NA | 300 | A | 15 | Alarm Level for Equip 300 Signal 15 -> NA
8 | 2021-04-01 12:58:18 | AR | - | NA | 300 | A | 15 | Alarm Relay output mapping for Equip 300 Signal 15 -> Relay NA
9 | 2021-04-01 13:00:43 | AL | - | CA | 701 | A | 26 | Alarm Level for Equip 701 Signal 26 -> CA
10 | 2021-04-01 13:00:43 | AR | - | 6 | 701 | A | 26 | Alarm Relay output mapping for Equip 701 Signal 26 -> Relay 6
11 | 2021-04-01 13:01:45 | AL | - | CA | 200 | A | 2 | Alarm Level for Equip 200 Signal 2 -> CA
12 | 2021-04-01 13:01:45 | AR | - | 7 | 200 | A | 2 | Alarm Relay output mapping for Equip 200 Signal 2 -> Relay 7
13 | 2021-04-01 13:02:47 | AL | - | CA | 200 | A | 3 | Alarm Level for Equip 200 Signal 3 -> CA
14 | 2021-04-01 13:02:47 | AR | - | 7 | 200 | A | 3 | Alarm Relay output mapping for Equip 200 Signal 3 -> Relay 7
15 | 2021-04-01 13:02:55 | AL | - | MA | 200 | A | 5 | Alarm Level for Equip 200 Signal 5 -> MA
16 | 2021-04-01 13:02:55 | AR | - | 7 | 200 | A | 5 | Alarm Relay output mapping for Equip 200 Signal 5 -> Relay 7
17 | 2021-04-01 13:04:03 | AL | - | MA | 201 | A | 1 | Alarm Level for Equip 201 Signal 1 -> MA
18 | 2021-04-01 13:04:03 | AR | - | 7 | 201 | A | 1 | Alarm Relay output mapping for Equip 201 Signal 1 -> Relay 7
19 | 2021-04-01 13:04:12 | AL | - | MA | 201 | A | 3 | Alarm Level for Equip 201 Signal 3 -> MA
20 | 2021-04-01 13:04:12 | AR | - | 7 | 201 | A | 3 | Alarm Relay output mapping for Equip 201 Signal 3 -> Relay 7
21 | 2021-04-01 13:04:21 | AL | - | OA | 201 | A | 5 | Alarm Level for Equip 201 Signal 5 -> OA
22 | 2021-04-01 13:04:21 | AR | - | 7 | 201 | A | 5 | Alarm Relay output mapping for Equip 201 Signal 5 -> Relay 7
23 | 2021-04-01 13:04:31 | AL | - | MA | 201 | A | 6 | Alarm Level for Equip 201 Signal 6 -> MA
24 | 2021-04-01 13:04:31 | AR | - | 7 | 201 | A | 6 | Alarm Relay output mapping for Equip 201 Signal 6 -> Relay 7
25 | 2021-04-01 13:04:40 | AL | - | MA | 201 | A | 9 | Alarm Level for Equip 201 Signal 9 -> MA
26 | 2021-04-01 13:04:40 | AR | - | 7 | 201 | A | 9 | Alarm Relay output mapping for Equip 201 Signal 9 -> Relay 7
27 | 2021-04-01 13:05:44 | AL | - | CA | 100 | A | 156 | Alarm Level for Equip 100 Signal 156 -> CA
28 | 2021-04-01 13:05:44 | AR | - | 8 | 100 | A | 156 | Alarm Relay output mapping for Equip 100 Signal 156 -> Relay 8
29 | 2021-04-01 13:05:54 | AL | - | CA | 100 | A | 157 | Alarm Level for Equip 100 Signal 157 -> CA
30 | 2021-04-01 13:05:54 | AR | - | 8 | 100 | A | 157 | Alarm Relay output mapping for Equip 100 Signal 157 -> Relay 8
31 | 2008-01-01 00:37:14 | ST | EF | BPP | - | - | - | Site Name change to: BPP
32 | 2008-01-01 00:37:28 | SD | EF | BPP | - | - | - | Site Description change to: BPP
33 | 2008-01-01 00:38:00 | SL | EF | Bangpongpang | - | - | - | Site Location change to: Bangpongpang
34 | 2021-07-05 13:18:14 | AL | - | CA | 701 | A | 26 | Alarm Level for Equip 701 Signal 26 -> CA
35 | 2021-07-05 13:18:14 | AR | - | 1 | 701 | A | 26 | Alarm Relay output mapping for Equip 701 Signal 26 -> Relay 1
36 | 2021-07-05 14:23:24 | AL | - | CA | 200 | A | 2 | Alarm Level for Equip 200 Signal 2 -> CA
37 | 2021-07-05 14:23:24 | AR | - | 2 | 200 | A | 2 | Alarm Relay output mapping for Equip 200 Signal 2 -> Relay 2
38 | 2021-07-05 14:23:30 | AL | - | CA | 200 | A | 3 | Alarm Level for Equip 200 Signal 3 -> CA
39 | 2021-07-05 14:23:30 | AR | - | 2 | 200 | A | 3 | Alarm Relay output mapping for Equip 200 Signal 3 -> Relay 2
40 | 2021-07-05 14:23:37 | AL | - | MA | 200 | A | 5 | Alarm Level for Equip 200 Signal 5 -> MA
41 | 2021-07-05 14:23:37 | AR | - | 2 | 200 | A | 5 | Alarm Relay output mapping for Equip 200 Signal 5 -> Relay 2
42 | 2021-07-05 14:24:03 | AL | - | MA | 201 | A | 1 | Alarm Level for Equip 201 Signal 1 -> MA
43 | 2021-07-05 14:24:03 | AR | - | 2 | 201 | A | 1 | Alarm Relay output mapping for Equip 201 Signal 1 -> Relay 2
44 | 2021-07-05 14:24:11 | AL | - | MA | 201 | A | 3 | Alarm Level for Equip 201 Signal 3 -> MA
45 | 2021-07-05 14:24:11 | AR | - | 2 | 201 | A | 3 | Alarm Relay output mapping for Equip 201 Signal 3 -> Relay 2
46 | 2021-07-05 14:24:19 | AL | - | OA | 201 | A | 5 | Alarm Level for Equip 201 Signal 5 -> OA
47 | 2021-07-05 14:24:19 | AR | - | 2 | 201 | A | 5 | Alarm Relay output mapping for Equip 201 Signal 5 -> Relay 2
48 | 2021-07-05 14:24:26 | AL | - | MA | 201 | A | 6 | Alarm Level for Equip 201 Signal 6 -> MA
49 | 2021-07-05 14:24:26 | AR | - | 2 | 201 | A | 6 | Alarm Relay output mapping for Equip 201 Signal 6 -> Relay 2
50 | 2021-07-05 14:24:33 | AL | - | MA | 201 | A | 9 | Alarm Level for Equip 201 Signal 9 -> MA
51 | 2021-07-05 14:24:33 | AR | - | 2 | 201 | A | 9 | Alarm Relay output mapping for Equip 201 Signal 9 -> Relay 2
52 | 2021-07-05 14:37:25 | AL | - | OA | 100 | A | 169 | Alarm Level for Equip 100 Signal 169 -> OA
53 | 2021-07-05 14:37:25 | AR | - | 3 | 100 | A | 169 | Alarm Relay output mapping for Equip 100 Signal 169 -> Relay 3
54 | 2021-07-05 14:58:34 | AL | - | CA | 100 | A | 157 | Alarm Level for Equip 100 Signal 157 -> CA
55 | 2021-07-05 14:58:34 | AR | - | 4 | 100 | A | 157 | Alarm Relay output mapping for Equip 100 Signal 157 -> Relay 4
56 | 2021-07-05 14:58:40 | AL | - | CA | 100 | A | 156 | Alarm Level for Equip 100 Signal 156 -> CA
57 | 2021-07-05 14:58:40 | AR | - | 4 | 100 | A | 156 | Alarm Relay output mapping for Equip 100 Signal 156 -> Relay 4
58 | 2021-07-05 23:42:30 | ST | EF | RBD | - | - | - | Site Name change to: RBD
59 | 2021-07-05 23:43:02 | SL | EF | Ratburana | - | - | - | Site Location change to: Ratburana
60 | 2021-07-05 23:43:13 | SD | EF | RBD | - | - | - | Site Description change to: RBD
61 | 2021-07-06 00:03:11 | AL | - | OA | 100 | A | 170 | Alarm Level for Equip 100 Signal 170 -> OA
62 | 2021-07-06 00:03:11 | AR | - | 3 | 100 | A | 170 | Alarm Relay output mapping for Equip 100 Signal 170 -> Relay 3
63 | 2021-07-06 00:17:50 | AL | - | OA | 300 | A | 24 | Alarm Level for Equip 300 Signal 24 -> OA
64 | 2021-07-06 00:17:50 | AR | - | 4 | 300 | A | 24 | Alarm Relay output mapping for Equip 300 Signal 24 -> Relay 4
65 | 2021-07-06 00:17:59 | AL | - | OA | 300 | A | 21 | Alarm Level for Equip 300 Signal 21 -> OA
66 | 2021-07-06 00:17:59 | AR | - | 4 | 300 | A | 21 | Alarm Relay output mapping for Equip 300 Signal 21 -> Relay 4
67 | 2021-07-06 00:18:13 | AL | - | OA | 300 | A | 24 | Alarm Level for Equip 300 Signal 24 -> OA
68 | 2021-07-06 00:18:13 | AR | - | NA | 300 | A | 24 | Alarm Relay output mapping for Equip 300 Signal 24 -> Relay NA
69 | 2021-07-06 00:18:22 | AL | - | OA | 300 | A | 21 | Alarm Level for Equip 300 Signal 21 -> OA
70 | 2021-07-06 00:18:22 | AR | - | NA | 300 | A | 21 | Alarm Relay output mapping for Equip 300 Signal 21 -> Relay NA
71 | 2021-07-06 00:47:10 | ST | EF | SDH | - | - | - | Site Name change to: SDH
72 | 2008-03-07 05:02:07 | ST | EF | JWC | - | - | - | Site Name change to: JWC
73 | 2008-03-07 05:02:12 | SD | EF | JWC | - | - | - | Site Description change to: JWC
74 | 2008-03-07 05:02:17 | SL | EF | MEA | - | - | - | Site Location change to: MEA
75 | 2021-07-20 19:46:17 | ST | EF | Jangwattana | - | - | - | Site Name change to: Jangwattana
76 | 2021-07-20 19:51:32 | AL | - | OA | 301 | A | 3 | Alarm Level for Equip 301 Signal 3 -> OA
77 | 2021-07-20 19:51:32 | AL | - | OA | 302 | A | 3 | Alarm Level for Equip 302 Signal 3 -> OA
78 | 2021-07-20 19:51:32 | AL | - | OA | 303 | A | 3 | Alarm Level for Equip 303 Signal 3 -> OA
79 | 2021-07-20 19:51:32 | AR | - | 4 | 301 | A | 3 | Alarm Relay output mapping for Equip 301 Signal 3 -> Relay 4
80 | 2021-07-20 19:52:35 | AL | - | MA | 201 | A | 1 | Alarm Level for Equip 201 Signal 1 -> MA
81 | 2021-07-20 19:52:35 | AR | - | 1 | 201 | A | 1 | Alarm Relay output mapping for Equip 201 Signal 1 -> Relay 1
82 | 2021-08-13 12:41:38 | SL | EF | Site Location | - | - | - | Site Location change to: Site Location
83 | 2021-08-13 12:41:43 | ST | EF | Site Name | - | - | - | Site Name change to: Site Name
84 | 2021-08-13 12:41:59 | SD | EF | NECODE | - | - | - | Site Description change to: NECODE
85 | 2021-08-13 12:42:06 | SL | EF | MEA | - | - | - | Site Location change to: MEA
86 | 2021-08-23 12:15:18 | SD | EF | SE | - | - | - | Site Description change to: SE
87 | 2021-08-23 12:15:52 | ST | EF | SRI-EIAM | - | - | - | Site Name change to: SRI-EIAM

## All Live Extractable Parameters
No. | Endpoint | Section / Path | Parameter Name | Equip ID | Sig Type | Sig ID | Signal Key | Value Type | Value (SE - 10.209.57.21) | Value (BAT - 10.209.1.21) | Unit / Options | Settable via API
1 | /var/datas/data.setting.html | CHARGE.list | Auto/Manual State | 1 | 2 | 7 | 1:2:7 | 5 | 0 | 0 | [['Auto', '自动'], ['Manual', '手动']] | Yes (POST web_cgi_control.cgi)
2 | /var/datas/data.setting.html | CHARGE.list | Battery Type Number | 115 | 2 | 30 | 115:2:30 | 3 | 1 | 1 |  | Yes (POST web_cgi_control.cgi)
3 | /var/datas/data.setting.html | CHARGE.list | Number of Battery Shunts | 115 | 2 | 64 | 115:2:64 | 5 | 1 | 1 | [['0', '0'], ['1', '1'], ['2', '2']] | Yes (POST web_cgi_control.cgi)
4 | /var/datas/data.setting.html | CHARGE.list | Action on Very High Battery Temp | 115 | 2 | 69 | 115:2:69 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Lowering Voltage', '调低输出电压']] | Yes (POST web_cgi_control.cgi)
5 | /var/datas/data.setting.html | CHARGE.list | Low Capacity Point | 115 | 2 | 60 | 115:2:60 | 2 | 75 | 75 | % | Yes (POST web_cgi_control.cgi)
6 | /var/datas/data.setting.html | CHARGE.list | Float Charge Voltage | 115 | 2 | 16 | 115:2:16 | 2 | 53.5 | 53.5 | V | Yes (POST web_cgi_control.cgi)
7 | /var/datas/data.setting.html | CHARGE.list | Equalize Charge Voltage | 115 | 2 | 17 | 115:2:17 | 2 | 53.6 | 53.6 | V | Yes (POST web_cgi_control.cgi)
8 | /var/datas/data.setting.html | CHARGE.list | Battery Current Limit | 115 | 2 | 29 | 115:2:29 | 2 | 0.10 | 0.10 | C10 | Yes (POST web_cgi_control.cgi)
9 | /var/datas/data.setting.html | CHARGE.list | Over Current Limit | 115 | 2 | 45 | 115:2:45 | 2 | 0.30 | 0.30 | C10 | Yes (POST web_cgi_control.cgi)
10 | /var/datas/data.setting.html | CHARGE.list | Automatic Equalize | 115 | 2 | 21 | 115:2:21 | 5 | 0 | 0 | [['No', '否'], ['Yes', '是']] | Yes (POST web_cgi_control.cgi)
11 | /var/datas/data.setting.html | CHARGE.list | Maximum Equalize Charge Time | 115 | 2 | 18 | 115:2:18 | 3 | 1080 | 1080 | min | Yes (POST web_cgi_control.cgi)
12 | /var/datas/data.setting.html | CHARGE.list | Equalize for Test | 115 | 2 | 44 | 115:2:44 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
13 | /var/datas/data.setting.html | CHARGE.list | Cyclic Equalize | 115 | 2 | 24 | 115:2:24 | 5 | 0 | 0 | [['No', '否'], ['Yes', '是']] | Yes (POST web_cgi_control.cgi)
14 | /var/datas/data.setting.html | CHARGE.list | Temperature Compensation Center | 115 | 2 | 27 | 115:2:27 | 2 | 25.0 | 25.0 | deg.C | Yes (POST web_cgi_control.cgi)
15 | /var/datas/data.setting.html | CHARGE.list | Temp Comp Coefficient (slope) | 115 | 2 | 28 | 115:2:28 | 2 | 72.0 | 72.0 | mV/deg.C | Yes (POST web_cgi_control.cgi)
16 | /var/datas/data.setting.html | CHARGE.list | Temp Comp Voltage Clamp | 115 | 2 | 198 | 115:2:198 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
17 | /var/datas/data.setting.html | CHARGE.list | Comp Temp High2 | 115 | 2 | 76 | 115:2:76 | 2 | 50 | 50 | deg.C | Yes (POST web_cgi_control.cgi)
18 | /var/datas/data.setting.html | CHARGE.list | Comp Temp High1 | 115 | 2 | 77 | 115:2:77 | 2 | 50 | 50 | deg.C | Yes (POST web_cgi_control.cgi)
19 | /var/datas/data.setting.html | CHARGE.list | Comp Temp Low | 115 | 2 | 78 | 115:2:78 | 2 | 0 | 0 | deg.C | Yes (POST web_cgi_control.cgi)
20 | /var/datas/data.setting.html | CHARGE.list | Calculate Battery Current | 115 | 2 | 73 | 115:2:73 | 5 | 0 | 0 | [['No', '否'], ['Yes', '是']] | Yes (POST web_cgi_control.cgi)
21 | /var/datas/data.setting.html | CHARGE.list | Over Voltage 1 | 1 | 2 | 187 | 1:2:187 | 2 | 55.7 | 55.7 | V | Yes (POST web_cgi_control.cgi)
22 | /var/datas/data.setting.html | CHARGE.list | Over Voltage 2 | 1 | 2 | 188 | 1:2:188 | 2 | 58.5 | 58.5 | V | Yes (POST web_cgi_control.cgi)
23 | /var/datas/data.setting.html | CHARGE.list | Under Voltage 1 | 1 | 2 | 189 | 1:2:189 | 2 | 48.0 | 48.0 | V | Yes (POST web_cgi_control.cgi)
24 | /var/datas/data.setting.html | CHARGE.list | Under Voltage 2 | 1 | 2 | 190 | 1:2:190 | 2 | 46.0 | 46.0 | V | Yes (POST web_cgi_control.cgi)
25 | /var/datas/data.setting.html | CHARGE.list | Curr Limited Mode | 115 | 2 | 62 | 115:2:62 | 5 | 1 | 1 | [['Disabled', '禁止'], ['Current', '电流方式'], ['Voltage', '电压方式']] | Yes (POST web_cgi_control.cgi)
26 | /var/datas/data.setting.html | CHARGE.list | Batt1 Rated Capacity | 116 | 2 | 10 | 116:2:10 | 2 | 100 | 100 | Ah | Yes (POST web_cgi_control.cgi)
27 | /var/datas/data.setting.html | CHARGE.list | Batt1 Shunt Current | 116 | 2 | 1 | 116:2:1 | 2 | 175.0 | 175.0 | A | Yes (POST web_cgi_control.cgi)
28 | /var/datas/data.setting.html | CHARGE.list | Batt1 Shunt Voltage | 116 | 2 | 2 | 116:2:2 | 2 | 25.0 | 25.0 | mV | Yes (POST web_cgi_control.cgi)
29 | /var/datas/data.setting.html | CHARGE.list | Rectifier Expansion | 1 | 2 | 180 | 1:2:180 | 5 | 0 | 0 | [['Inactive', '独立模式'], ['Primary', '主机模式'], ['Secondary', '从机模式']] | Yes (POST web_cgi_control.cgi)
30 | /var/datas/data.setting.html | CHARGE.list | Equalize/Float Charge Control | 115 | 1 | 1 | 115:1:1 | 5 | 0 | 0 | [['Float Charge', '浮充'], ['Equalize Charge', '均充']] | Yes (POST web_cgi_control.cgi)
31 | /var/datas/data.setting.html | CHARGE.list | Clear Abnormal Bat Current Alarm | 115 | 1 | 8 | 115:1:8 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
32 | /var/datas/data.setting.html | CHARGE.list | SMDU-EIB Mode | 1 | 2 | 452 | 1:2:452 | 5 | 0 | 0 | [['Normal', '正常'], ['Load Switch', '负载开关']] | Yes (POST web_cgi_control.cgi)
33 | /var/datas/data.setting.html | CHARGE.list | Outgoing Alarms Blocked | 1 | 2 | 8 | 1:2:8 | 5 | 0 | 0 | [['Normal', '正常'], ['Blocked', '阻塞']] | Yes (POST web_cgi_control.cgi)
34 | /var/datas/data.setting.html | CHARGE.list | Reset Battery Capacity | 115 | 1 | 7 | 115:1:7 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
35 | /var/datas/data.setting.html | CHARGE.list | CB Threshold Value | 1 | 2 | 477 | 1:2:477 | 2 | 70 | 70 | % | Yes (POST web_cgi_control.cgi)
36 | /var/datas/data.setting.html | CHARGE.list | CB Overload Value | 1 | 2 | 478 | 1:2:478 | 2 | 80 | 80 | % | Yes (POST web_cgi_control.cgi)
37 | /var/datas/data.setting.html | CHARGE.list | DisCharging Alarm Curr threshold | 115 | 2 | 170 | 115:2:170 | 2 | 2.0 | 2.0 | A | Yes (POST web_cgi_control.cgi)
38 | /var/datas/data.setting.html | CHARGE.list | Upper Limit | 115 | 2 | 430 | 115:2:430 | 2 | 0.110 | 0.110 | C10 | Yes (POST web_cgi_control.cgi)
39 | /var/datas/data.setting.html | CHARGE.list | Stable Range Upper Limit | 115 | 2 | 431 | 115:2:431 | 2 | 1.00 | 1.00 |  | Yes (POST web_cgi_control.cgi)
40 | /var/datas/data.setting.html | CHARGE.list | Stable Range Lower Limit | 115 | 2 | 432 | 115:2:432 | 2 | 0.95 | 0.95 |  | Yes (POST web_cgi_control.cgi)
41 | /var/datas/data.setting.html | CHARGE.list | Speed Set Point | 115 | 2 | 433 | 115:2:433 | 2 | 0.50 | 0.50 |  | Yes (POST web_cgi_control.cgi)
42 | /var/datas/data.setting.html | CHARGE.list | Slow Speed Coefficient | 115 | 2 | 434 | 115:2:434 | 2 | 1.00 | 1.00 |  | Yes (POST web_cgi_control.cgi)
43 | /var/datas/data.setting.html | CHARGE.list | Fast Speed Coefficient | 115 | 2 | 435 | 115:2:435 | 2 | 1.00 | 1.00 |  | Yes (POST web_cgi_control.cgi)
44 | /var/datas/data.setting.html | CHARGE.list | Min Amplitude | 115 | 2 | 436 | 115:2:436 | 2 | 0.001 | 0.001 | V/C10/Cell | Yes (POST web_cgi_control.cgi)
45 | /var/datas/data.setting.html | CHARGE.list | Max Amplitude | 115 | 2 | 437 | 115:2:437 | 2 | 0.040 | 0.040 | V/C10/Cell | Yes (POST web_cgi_control.cgi)
46 | /var/datas/data.setting.html | CHARGE.list | Cycle Number | 115 | 2 | 438 | 115:2:438 | 3 | 1 | 1 | 10s | Yes (POST web_cgi_control.cgi)
47 | /var/datas/data.setting.html | CHARGE.list | Min Voltage BCL | 115 | 2 | 441 | 115:2:441 | 2 | 47.0 | 47.0 | V | Yes (POST web_cgi_control.cgi)
48 | /var/datas/data.setting.html | ECO.list | ECO Mode | 2 | 2 | 22 | 2:2:22 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
49 | /var/datas/data.setting.html | ECO.list | Reset Cycle Alarm | 2 | 1 | 11 | 2:1:11 | 5 | 1 | 1 | [['Clear', '清除']] | Yes (POST web_cgi_control.cgi)
50 | /var/datas/data.setting.html | LVD.list | LVD 1 | 187 | 2 | 3 | 187:2:3 | 5 | 1 | 1 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
51 | /var/datas/data.setting.html | LVD.list | LVD 1 Mode | 187 | 2 | 4 | 187:2:4 | 5 | 0 | 0 | [['Voltage', '电压方式'], ['Time', '时间方式']] | Yes (POST web_cgi_control.cgi)
52 | /var/datas/data.setting.html | LVD.list | LVD 1 Voltage | 187 | 2 | 1 | 187:2:1 | 2 | 43.2 | 43.2 | V | Yes (POST web_cgi_control.cgi)
53 | /var/datas/data.setting.html | LVD.list | LVD 1 Reconnect Voltage | 187 | 2 | 2 | 187:2:2 | 2 | 49.0 | 49.0 | V | Yes (POST web_cgi_control.cgi)
54 | /var/datas/data.setting.html | LVD.list | LVD 1 Reconnect Delay | 187 | 2 | 5 | 187:2:5 | 3 | 2 | 2 | min | Yes (POST web_cgi_control.cgi)
55 | /var/datas/data.setting.html | LVD.list | LVD 1 Time | 187 | 2 | 18 | 187:2:18 | 3 | 300 | 300 | min | Yes (POST web_cgi_control.cgi)
56 | /var/datas/data.setting.html | LVD.list | LVD 1 Dependency | 187 | 2 | 20 | 187:2:20 | 5 | 0 | 0 | [['None', '无'], ['LVD 1', 'LVD 1'], ['LVD 2', 'LVD 2'], ['LVD 3', 'LVD 3']] | Yes (POST web_cgi_control.cgi)
57 | /var/datas/data.setting.html | LVD.list | LVD 2 | 187 | 2 | 8 | 187:2:8 | 5 | 1 | 1 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
58 | /var/datas/data.setting.html | LVD.list | LVD 2 Mode | 187 | 2 | 9 | 187:2:9 | 5 | 0 | 0 | [['Voltage', '电压方式'], ['Time', '时间方式']] | Yes (POST web_cgi_control.cgi)
59 | /var/datas/data.setting.html | LVD.list | LVD 2 Voltage | 187 | 2 | 6 | 187:2:6 | 2 | 43.2 | 43.2 | V | Yes (POST web_cgi_control.cgi)
60 | /var/datas/data.setting.html | LVD.list | LVD 2 Reconnect Voltage | 187 | 2 | 7 | 187:2:7 | 2 | 49.0 | 49.0 | V | Yes (POST web_cgi_control.cgi)
61 | /var/datas/data.setting.html | LVD.list | LVD 2 Reconnect Delay | 187 | 2 | 10 | 187:2:10 | 3 | 2 | 2 | min | Yes (POST web_cgi_control.cgi)
62 | /var/datas/data.setting.html | LVD.list | LVD 2 Time | 187 | 2 | 19 | 187:2:19 | 3 | 600 | 600 | min | Yes (POST web_cgi_control.cgi)
63 | /var/datas/data.setting.html | LVD.list | LVD 2 Dependency | 187 | 2 | 21 | 187:2:21 | 5 | 0 | 0 | [['None', '无'], ['LVD 1', 'LVD 1'], ['LVD 2', 'LVD 2'], ['LVD 3', 'LVD 3']] | Yes (POST web_cgi_control.cgi)
64 | /var/datas/data.setting.html | LVD.list | High Temp Disconnect 1 | 187 | 2 | 11 | 187:2:11 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
65 | /var/datas/data.setting.html | LVD.list | High Temp Disconnect 2 | 187 | 2 | 12 | 187:2:12 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
66 | /var/datas/data.setting.html | LVD.list | LVD Contactor Type | 187 | 2 | 14 | 187:2:14 | 5 | 1 | 1 | [['Bistable', '双稳'], ['Mono-Stable', '单稳'], ['Mono w/Sample', '单稳带回采']] | Yes (POST web_cgi_control.cgi)
67 | /var/datas/data.setting.html | RECT.list | Rectifier Current Limit | 2 | 1 | 1 | 2:1:1 | 2 | 121 | 121 | % | Yes (POST web_cgi_control.cgi)
68 | /var/datas/data.setting.html | RECT.list | Rectifier Trim | 2 | 1 | 2 | 2:1:2 | 2 | 53 | 53.2 | V | Yes (POST web_cgi_control.cgi)
69 | /var/datas/data.setting.html | RECT.list | DC On/Off Control | 2 | 1 | 3 | 2:1:3 | 5 | 0 | 0 | [['Switch On All', '开所有模块'], ['Switch Off All', '关所有模块']] | Yes (POST web_cgi_control.cgi)
70 | /var/datas/data.setting.html | RECT.list | AC On/Off Control | 2 | 1 | 4 | 2:1:4 | 5 | 0 | 0 | [['Switch On All', '开所有模块'], ['Switch Off All', '关所有模块']] | Yes (POST web_cgi_control.cgi)
71 | /var/datas/data.setting.html | RECT.list | Rectifiers LED Control | 2 | 1 | 5 | 2:1:5 | 5 | 0 | 0 | [['Stop Flashing', '全部灯不闪'], ['All Flashing', '全部灯闪']] | Yes (POST web_cgi_control.cgi)
72 | /var/datas/data.setting.html | RECT.list | Fan Speed Control | 2 | 1 | 6 | 2:1:6 | 5 | 0 | 0 | [['Automatic Speed', '自动调速'], ['Full Speed', '全速']] | Yes (POST web_cgi_control.cgi)
73 | /var/datas/data.setting.html | RECT.list | Clear Rectifier Lost Alarm | 2 | 1 | 8 | 2:1:8 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
74 | /var/datas/data.setting.html | RECT.list | Confirm Rectifier ID/Phase | 2 | 1 | 13 | 2:1:13 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
75 | /var/datas/data.setting.html | RECT.list | Clear Rectifier Comm Fail Alarm | 2 | 1 | 14 | 2:1:14 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
76 | /var/datas/data.setting.html | RECT.list | Reset Rectifier IDs | 2 | 1 | 17 | 2:1:17 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
77 | /var/datas/data.setting.html | RECT.list | HVSD Limit | 2 | 2 | 3 | 2:2:3 | 2 | 59.0 | 59.0 | V | Yes (POST web_cgi_control.cgi)
78 | /var/datas/data.setting.html | RECT.list | HVSD Restart Time | 2 | 2 | 6 | 2:2:6 | 3 | 300 | 300 | s | Yes (POST web_cgi_control.cgi)
79 | /var/datas/data.setting.html | RECT.list | Restart on HVSD | 2 | 2 | 30 | 2:2:30 | 5 | 1 | 1 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
80 | /var/datas/data.setting.html | RECT.list | Sequence Start Interval | 2 | 2 | 31 | 2:2:31 | 3 | 0 | 0 | s | Yes (POST web_cgi_control.cgi)
81 | /var/datas/data.setting.html | RECT.list | Walk-In | 2 | 2 | 8 | 2:2:8 | 5 | 1 | 1 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
82 | /var/datas/data.setting.html | RECT.list | Walk-In Time | 2 | 2 | 7 | 2:2:7 | 3 | 8 | 8 | s | Yes (POST web_cgi_control.cgi)
83 | /var/datas/data.setting.html | RECT.list | Turn On when AC Over Voltage | 2 | 2 | 19 | 2:2:19 | 5 | 0 | 0 | [['Yes', '是'], ['No', '否']] | Yes (POST web_cgi_control.cgi)
84 | /var/datas/data.setting.html | RECT.list | Input Current Limit | 2 | 2 | 33 | 2:2:33 | 2 | 30.0 | 30.0 | A | Yes (POST web_cgi_control.cgi)
85 | /var/datas/data.setting.html | RECT.list | MixHE Power | 2 | 2 | 38 | 2:2:38 | 5 | 0 | 0 | [['Derated', '降额'], ['Non-Derated', '不降']] | Yes (POST web_cgi_control.cgi)
86 | /var/datas/data.setting.html | RECT.list | HVSD | 2 | 2 | 41 | 2:2:41 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
87 | /var/datas/data.setting.html | RECT.list | Diesel Generator Power Limit | 2 | 2 | 43 | 2:2:43 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
88 | /var/datas/data.setting.html | RECT.list | Diesel Generator Digital Input | 2 | 2 | 44 | 2:2:44 | 5 | 0 | 0 | [['None', '无'], ['Digital Input 1', '开关量 1'], ['Digital Input 2', '开关量 2'], ['Digital Input 3', '开关量 3'], ['Digital Input 4', '开关量 4'], ['Digital Input 5', '开关量 5'], ['Digital Input 6', '开关量 6'], ['Digital Input 7', '开关量 7'], ['Digital Input 8', '开关量 8']] | Yes (POST web_cgi_control.cgi)
89 | /var/datas/data.setting.html | RECT.list | Diesel Gen Power Limit Point Set | 2 | 2 | 45 | 2:2:45 | 2 | 40.0 | 40.0 | % | Yes (POST web_cgi_control.cgi)
90 | /var/datas/data.setting.html | RECT.list | Current Limit | 2 | 2 | 47 | 2:2:47 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
91 | /var/datas/data.setting.html | RECT.list | Normal Update | 2 | 2 | 54 | 2:2:54 | 5 | 0 | 0 | [['No', '否'], ['Yes', '是']] | Yes (POST web_cgi_control.cgi)
92 | /var/datas/data.setting.html | RECT.list | Force Update | 2 | 2 | 55 | 2:2:55 | 5 | 0 | 0 | [['No', '否'], ['Yes', '是']] | Yes (POST web_cgi_control.cgi)
93 | /var/datas/data.setting.html | RECT.list | Default Voltage | 2 | 2 | 58 | 2:2:58 | 2 | 53.5 | 53.5 | V | Yes (POST web_cgi_control.cgi)
94 | /var/datas/data.setting.html | RECT.list | HVSD LVD1 Disconn Enable | 2 | 2 | 60 | 2:2:60 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
95 | /var/datas/data.setting.html | RECT.list | Clear ACDC kWh | 2 | 1 | 18 | 2:1:18 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
96 | /var/datas/data.setting.html | BATT_TEST.list | AC Fail Test | 115 | 2 | 11 | 115:2:11 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
97 | /var/datas/data.setting.html | BATT_TEST.list | Constant Current Test | 115 | 2 | 8 | 115:2:8 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
98 | /var/datas/data.setting.html | BATT_TEST.list | Short Test | 115 | 2 | 12 | 115:2:12 | 5 | 0 | 0 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
99 | /var/datas/data.setting.html | BATT_TEST.list | Test Voltage Level | 115 | 2 | 46 | 115:2:46 | 2 | 45.0 | 45.0 | V | Yes (POST web_cgi_control.cgi)
100 | /var/datas/data.setting.html | BATT_TEST.list | End Test Voltage | 115 | 2 | 6 | 115:2:6 | 2 | 45.2 | 45.2 | V | Yes (POST web_cgi_control.cgi)
101 | /var/datas/data.setting.html | BATT_TEST.list | End Test Time | 115 | 2 | 5 | 115:2:5 | 3 | 150 | 30 | min | Yes (POST web_cgi_control.cgi)
102 | /var/datas/data.setting.html | BATT_TEST.list | End Test Capacity | 115 | 2 | 7 | 115:2:7 | 2 | 70.0 | 70.0 | % | Yes (POST web_cgi_control.cgi)
103 | /var/datas/data.setting.html | BATT_TEST.list | Record Threshold | 115 | 2 | 43 | 115:2:43 | 2 | 0.100 | 0.100 | V | Yes (POST web_cgi_control.cgi)
104 | /var/datas/data.setting.html | BATT_TEST.list | Number of Planned Tests per Year | 115 | 2 | 47 | 115:2:47 | 3 | 12 | 12 |  | Yes (POST web_cgi_control.cgi)
105 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 1 (MM-DD Hr) | 115 | 2 | 48 | 115:2:48 | 4 | 63072450 | 63072450 |  | Yes (POST web_cgi_control.cgi)
106 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 2 (MM-DD Hr) | 115 | 2 | 49 | 115:2:49 | 4 | 65750850 | 65750850 |  | Yes (POST web_cgi_control.cgi)
107 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 3 (MM-DD Hr) | 115 | 2 | 50 | 115:2:50 | 4 | 68256450 | 68256450 |  | Yes (POST web_cgi_control.cgi)
108 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 4 (MM-DD Hr) | 115 | 2 | 51 | 115:2:51 | 4 | 70934850 | 70934850 |  | Yes (POST web_cgi_control.cgi)
109 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 5 (MM-DD Hr) | 115 | 2 | 52 | 115:2:52 | 4 | 73526850 | 73526850 |  | Yes (POST web_cgi_control.cgi)
110 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 6 (MM-DD Hr) | 115 | 2 | 53 | 115:2:53 | 4 | 76223250 | 76205250 |  | Yes (POST web_cgi_control.cgi)
111 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 7 (MM-DD Hr) | 115 | 2 | 54 | 115:2:54 | 4 | 78797250 | 78797250 |  | Yes (POST web_cgi_control.cgi)
112 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 8 (MM-DD Hr) | 115 | 2 | 55 | 115:2:55 | 4 | 81475650 | 81475650 |  | Yes (POST web_cgi_control.cgi)
113 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 9 (MM-DD Hr) | 115 | 2 | 56 | 115:2:56 | 4 | 84154050 | 84154050 |  | Yes (POST web_cgi_control.cgi)
114 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 10 (MM-DD Hr) | 115 | 2 | 57 | 115:2:57 | 4 | 86746050 | 86746050 |  | Yes (POST web_cgi_control.cgi)
115 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 11 (MM-DD Hr) | 115 | 2 | 58 | 115:2:58 | 4 | 89424450 | 89424450 |  | Yes (POST web_cgi_control.cgi)
116 | /var/datas/data.setting.html | BATT_TEST.list | Planned Test 12 (MM-DD Hr) | 115 | 2 | 59 | 115:2:59 | 4 | 92016450 | 92016450 |  | Yes (POST web_cgi_control.cgi)
117 | /var/datas/data.setting.html | BATT_TEST.list | Battery Test Control | 115 | 1 | 2 | 115:1:2 | 5 | 0 | 0 | [['Stop', '停止'], ['Start', '开始']] | Yes (POST web_cgi_control.cgi)
118 | /var/datas/data.setting.html | BATT_TEST.list | Clear Bad Battery Alarm | 115 | 1 | 3 | 115:1:3 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
119 | /var/datas/data.setting.html | BATT_TEST.list | Clear Battery Test Fail Alarm | 115 | 1 | 10 | 115:1:10 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
120 | /var/datas/data.setting.html | BATT_TEST.list | Clear Discharge Curr Imbalance | 115 | 1 | 9 | 115:1:9 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
121 | /var/datas/data.setting.html | TEMPERATURE.list | Ambient Temp Sensor | 1 | 2 | 208 | 1:2:208 | 5 | 3 | 3 | [['None', '无'], ['Maximum', '最大温度'], ['Average', '平均温度'], ['System Temp1', '系统温度1'], ['System Temp2', '系统温度2'], ['System Temp3', '系统温度3'], ['IB2 Temp1', 'IB2温度1'], ['IB2 Temp2', 'IB2温度2'], ['EIB Temp1', 'EIB温度1'], ['EIB Temp2', 'EIB温度2'], ['SMTemp1 Temp1', 'SMTemp1温度1'], ['SMTemp1 Temp2', 'SMTemp1温度2'], ['SMTemp1 Temp3', 'SMTemp1温度3'], ['SMTemp1 Temp4', 'SMTemp1温度4'], ['SMTemp1 Temp5', 'SMTemp1温度5'], ['SMTemp1 Temp6', 'SMTemp1温度6'], ['SMTemp1 Temp7', 'SMTemp1温度7'], ['SMTemp1 Temp8', 'SMTemp1温度8'], ['SMTemp2 Temp1', 'SMTemp2温度1'], ['SMTemp2 Temp2', 'SMTemp2温度2'], ['SMTemp2 Temp3', 'SMTemp2温度3'], ['SMTemp2 Temp4', 'SMTemp2温度4'], ['SMTemp2 Temp5', 'SMTemp2温度5'], ['SMTemp2 Temp6', 'SMTemp2温度6'], ['SMTemp2 Temp7', 'SMTemp2温度7'], ['SMTemp2 Temp8', 'SMTemp2温度8'], ['SMTemp3 Temp1', 'SMTemp3温度1'], ['SMTemp3 Temp2', 'SMTemp3温度2'], ['SMTemp3 Temp3', 'SMTemp3温度3'], ['SMTemp3 Temp4', 'SMTemp3温度4'], ['SMTemp3 Temp5', 'SMTemp3温度5'], ['SMTemp3 Temp6', 'SMTemp3温度6'], ['SMTemp3 Temp7', 'SMTemp3温度7'], ['SMTemp3 Temp8', 'SMTemp3温度8'], ['SMTemp4 Temp1', 'SMTemp4温度1'], ['SMTemp4 Temp2', 'SMTemp4温度2'], ['SMTemp4 Temp3', 'SMTemp4温度3'], ['SMTemp4 Temp4', 'SMTemp4温度4'], ['SMTemp4 Temp5', 'SMTemp4温度5'], ['SMTemp4 Temp6', 'SMTemp4温度6'], ['SMTemp4 Temp7', 'SMTemp4温度7'], ['SMTemp4 Temp8', 'SMTemp4温度8'], ['SMTemp5 Temp1', 'SMTemp5温度1'], ['SMTemp5 Temp2', 'SMTemp5温度2'], ['SMTemp5 Temp3', 'SMTemp5温度3'], ['SMTemp5 Temp4', 'SMTemp5温度4'], ['SMTemp5 Temp5', 'SMTemp5温度5'], ['SMTemp5 Temp6', 'SMTemp5温度6'], ['SMTemp5 Temp7', 'SMTemp5温度7'], ['SMTemp5 Temp8', 'SMTemp5温度8'], ['SMTemp6 Temp1', 'SMTemp6温度1'], ['SMTemp6 Temp2', 'SMTemp6温度2'], ['SMTemp6 Temp3', 'SMTemp6温度3'], ['SMTemp6 Temp4', 'SMTemp6温度4'], ['SMTemp6 Temp5', 'SMTemp6温度5'], ['SMTemp6 Temp6', 'SMTemp6温度6'], ['SMTemp6 Temp7', 'SMTemp6温度7'], ['SMTemp6 Temp8', 'SMTemp6温度8'], ['SMTemp7 Temp1', 'SMTemp7温度1'], ['SMTemp7 Temp2', 'SMTemp7温度2'], ['SMTemp7 Temp3', 'SMTemp7温度3'], ['SMTemp7 Temp4', 'SMTemp7温度4'], ['SMTemp7 Temp5', 'SMTemp7温度5'], ['SMTemp7 Temp6', 'SMTemp7温度6'], ['SMTemp7 Temp7', 'SMTemp7温度7'], ['SMTemp7 Temp8', 'SMTemp7温度8'], ['SMTemp8 Temp1', 'SMTemp8温度1'], ['SMTemp8 Temp2', 'SMTemp8温度2'], ['SMTemp8 Temp3', 'SMTemp8温度3'], ['SMTemp8 Temp4', 'SMTemp8温度4'], ['SMTemp8 Temp5', 'SMTemp8温度5'], ['SMTemp8 Temp6', 'SMTemp8温度6'], ['SMTemp8 Temp7', 'SMTemp8温度7'], ['SMTemp8 Temp8', 'SMTemp8温度8']] | Yes (POST web_cgi_control.cgi)
122 | /var/datas/data.setting.html | TEMPERATURE.list | Ambient Temp High1 | 1 | 2 | 209 | 1:2:209 | 2 | 38 | 38 | deg.C | Yes (POST web_cgi_control.cgi)
123 | /var/datas/data.setting.html | TEMPERATURE.list | Ambient Temp Low | 1 | 2 | 210 | 1:2:210 | 2 | 15 | 15 | deg.C | Yes (POST web_cgi_control.cgi)
124 | /var/datas/data.setting.html | TEMPERATURE.list | Ambient Temp High2 | 1 | 2 | 219 | 1:2:219 | 2 | 40 | 40 | deg.C | Yes (POST web_cgi_control.cgi)
125 | /var/datas/data.setting.html | TEMPERATURE.list | System Temp 1 | 1 | 2 | 50 | 1:2:50 | 5 | 1 | 1 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
126 | /var/datas/data.setting.html | TEMPERATURE.list | System Temp 2 | 1 | 2 | 51 | 1:2:51 | 5 | 2 | 2 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
127 | /var/datas/data.setting.html | TEMPERATURE.list | System Temp 3 | 1 | 2 | 52 | 1:2:52 | 5 | 0 | 0 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
128 | /var/datas/data.setting.html | TEMPERATURE.list | IB2 Temp 1 | 1 | 2 | 53 | 1:2:53 | 5 | 0 | 0 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
129 | /var/datas/data.setting.html | TEMPERATURE.list | IB2 Temp 2 | 1 | 2 | 54 | 1:2:54 | 5 | 0 | 0 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
130 | /var/datas/data.setting.html | TEMPERATURE.list | EIB Temp 1 | 1 | 2 | 78 | 1:2:78 | 5 | 0 | 0 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
131 | /var/datas/data.setting.html | TEMPERATURE.list | EIB Temp 2 | 1 | 2 | 79 | 1:2:79 | 5 | 0 | 0 | [['None', '未定义'], ['Ambient', '环境'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
132 | /var/datas/data.setting.html | TEMPERATURE.list | Temp Compensation Probe Number | 115 | 2 | 63 | 115:2:63 | 5 | 5 | 5 | [['None', '无'], ['Maximum', '最大温度'], ['Average', '平均温度'], ['Average SMBRC', 'SMBRC平均温度'], ['System Temp1', '系统温度1'], ['System Temp2', '系统温度2'], ['System Temp3', '系统温度3'], ['IB2 Temp1', 'IB2温度1'], ['IB2 Temp2', 'IB2温度2'], ['EIB Temp1', 'EIB温度1'], ['EIB Temp2', 'EIB温度2'], ['SMTemp1 Temp1', 'SMTemp1温度1'], ['SMTemp1 Temp2', 'SMTemp1温度2'], ['SMTemp1 Temp3', 'SMTemp1温度3'], ['SMTemp1 Temp4', 'SMTemp1温度4'], ['SMTemp1 Temp5', 'SMTemp1温度5'], ['SMTemp1 Temp6', 'SMTemp1温度6'], ['SMTemp1 Temp7', 'SMTemp1温度7'], ['SMTemp1 Temp8', 'SMTemp1温度8'], ['SMTemp2 Temp1', 'SMTemp2温度1'], ['SMTemp2 Temp2', 'SMTemp2温度2'], ['SMTemp2 Temp3', 'SMTemp2温度3'], ['SMTemp2 Temp4', 'SMTemp2温度4'], ['SMTemp2 Temp5', 'SMTemp2温度5'], ['SMTemp2 Temp6', 'SMTemp2温度6'], ['SMTemp2 Temp7', 'SMTemp2温度7'], ['SMTemp2 Temp8', 'SMTemp2温度8'], ['SMTemp3 Temp1', 'SMTemp3温度1'], ['SMTemp3 Temp2', 'SMTemp3温度2'], ['SMTemp3 Temp3', 'SMTemp3温度3'], ['SMTemp3 Temp4', 'SMTemp3温度4'], ['SMTemp3 Temp5', 'SMTemp3温度5'], ['SMTemp3 Temp6', 'SMTemp3温度6'], ['SMTemp3 Temp7', 'SMTemp3温度7'], ['SMTemp3 Temp8', 'SMTemp3温度8'], ['SMTemp4 Temp1', 'SMTemp4温度1'], ['SMTemp4 Temp2', 'SMTemp4温度2'], ['SMTemp4 Temp3', 'SMTemp4温度3'], ['SMTemp4 Temp4', 'SMTemp4温度4'], ['SMTemp4 Temp5', 'SMTemp4温度5'], ['SMTemp4 Temp6', 'SMTemp4温度6'], ['SMTemp4 Temp7', 'SMTemp4温度7'], ['SMTemp4 Temp8', 'SMTemp4温度8'], ['SMTemp5 Temp1', 'SMTemp5温度1'], ['SMTemp5 Temp2', 'SMTemp5温度2'], ['SMTemp5 Temp3', 'SMTemp5温度3'], ['SMTemp5 Temp4', 'SMTemp5温度4'], ['SMTemp5 Temp5', 'SMTemp5温度5'], ['SMTemp5 Temp6', 'SMTemp5温度6'], ['SMTemp5 Temp7', 'SMTemp5温度7'], ['SMTemp5 Temp8', 'SMTemp5温度8'], ['SMTemp6 Temp1', 'SMTemp6温度1'], ['SMTemp6 Temp2', 'SMTemp6温度2'], ['SMTemp6 Temp3', 'SMTemp6温度3'], ['SMTemp6 Temp4', 'SMTemp6温度4'], ['SMTemp6 Temp5', 'SMTemp6温度5'], ['SMTemp6 Temp6', 'SMTemp6温度6'], ['SMTemp6 Temp7', 'SMTemp6温度7'], ['SMTemp6 Temp8', 'SMTemp6温度8'], ['SMTemp7 Temp1', 'SMTemp7温度1'], ['SMTemp7 Temp2', 'SMTemp7温度2'], ['SMTemp7 Temp3', 'SMTemp7温度3'], ['SMTemp7 Temp4', 'SMTemp7温度4'], ['SMTemp7 Temp5', 'SMTemp7温度5'], ['SMTemp7 Temp6', 'SMTemp7温度6'], ['SMTemp7 Temp7', 'SMTemp7温度7'], ['SMTemp7 Temp8', 'SMTemp7温度8'], ['SMTemp8 Temp1', 'SMTemp8温度1'], ['SMTemp8 Temp2', 'SMTemp8温度2'], ['SMTemp8 Temp3', 'SMTemp8温度3'], ['SMTemp8 Temp4', 'SMTemp8温度4'], ['SMTemp8 Temp5', 'SMTemp8温度5'], ['SMTemp8 Temp6', 'SMTemp8温度6'], ['SMTemp8 Temp7', 'SMTemp8温度7'], ['SMTemp8 Temp8', 'SMTemp8温度8']] | Yes (POST web_cgi_control.cgi)
133 | /var/datas/data.setting.html | TEMPERATURE.list | BTRM Temp Sensor | 115 | 2 | 414 | 115:2:414 | 5 | 0 | 0 | [['None', '无'], ['Maximum', '最大温度'], ['Average', '平均温度'], ['Average SMBRC', 'SMBRC平均温度'], ['System Temp1', '系统温度1'], ['System Temp2', '系统温度2'], ['System Temp3', '系统温度3'], ['IB2 Temp1', 'IB2温度1'], ['IB2 Temp2', 'IB2温度2'], ['EIB Temp1', 'EIB温度1'], ['EIB Temp2', 'EIB温度2'], ['SMTemp1 Temp1', 'SMTemp1温度1'], ['SMTemp1 Temp2', 'SMTemp1温度2'], ['SMTemp1 Temp3', 'SMTemp1温度3'], ['SMTemp1 Temp4', 'SMTemp1温度4'], ['SMTemp1 Temp5', 'SMTemp1温度5'], ['SMTemp1 Temp6', 'SMTemp1温度6'], ['SMTemp1 Temp7', 'SMTemp1温度7'], ['SMTemp1 Temp8', 'SMTemp1温度8'], ['SMTemp2 Temp1', 'SMTemp2温度1'], ['SMTemp2 Temp2', 'SMTemp2温度2'], ['SMTemp2 Temp3', 'SMTemp2温度3'], ['SMTemp2 Temp4', 'SMTemp2温度4'], ['SMTemp2 Temp5', 'SMTemp2温度5'], ['SMTemp2 Temp6', 'SMTemp2温度6'], ['SMTemp2 Temp7', 'SMTemp2温度7'], ['SMTemp2 Temp8', 'SMTemp2温度8'], ['SMTemp3 Temp1', 'SMTemp3温度1'], ['SMTemp3 Temp2', 'SMTemp3温度2'], ['SMTemp3 Temp3', 'SMTemp3温度3'], ['SMTemp3 Temp4', 'SMTemp3温度4'], ['SMTemp3 Temp5', 'SMTemp3温度5'], ['SMTemp3 Temp6', 'SMTemp3温度6'], ['SMTemp3 Temp7', 'SMTemp3温度7'], ['SMTemp3 Temp8', 'SMTemp3温度8'], ['SMTemp4 Temp1', 'SMTemp4温度1'], ['SMTemp4 Temp2', 'SMTemp4温度2'], ['SMTemp4 Temp3', 'SMTemp4温度3'], ['SMTemp4 Temp4', 'SMTemp4温度4'], ['SMTemp4 Temp5', 'SMTemp4温度5'], ['SMTemp4 Temp6', 'SMTemp4温度6'], ['SMTemp4 Temp7', 'SMTemp4温度7'], ['SMTemp4 Temp8', 'SMTemp4温度8'], ['SMTemp5 Temp1', 'SMTemp5温度1'], ['SMTemp5 Temp2', 'SMTemp5温度2'], ['SMTemp5 Temp3', 'SMTemp5温度3'], ['SMTemp5 Temp4', 'SMTemp5温度4'], ['SMTemp5 Temp5', 'SMTemp5温度5'], ['SMTemp5 Temp6', 'SMTemp5温度6'], ['SMTemp5 Temp7', 'SMTemp5温度7'], ['SMTemp5 Temp8', 'SMTemp5温度8'], ['SMTemp6 Temp1', 'SMTemp6温度1'], ['SMTemp6 Temp2', 'SMTemp6温度2'], ['SMTemp6 Temp3', 'SMTemp6温度3'], ['SMTemp6 Temp4', 'SMTemp6温度4'], ['SMTemp6 Temp5', 'SMTemp6温度5'], ['SMTemp6 Temp6', 'SMTemp6温度6'], ['SMTemp6 Temp7', 'SMTemp6温度7'], ['SMTemp6 Temp8', 'SMTemp6温度8'], ['SMTemp7 Temp1', 'SMTemp7温度1'], ['SMTemp7 Temp2', 'SMTemp7温度2'], ['SMTemp7 Temp3', 'SMTemp7温度3'], ['SMTemp7 Temp4', 'SMTemp7温度4'], ['SMTemp7 Temp5', 'SMTemp7温度5'], ['SMTemp7 Temp6', 'SMTemp7温度6'], ['SMTemp7 Temp7', 'SMTemp7温度7'], ['SMTemp7 Temp8', 'SMTemp7温度8'], ['SMTemp8 Temp1', 'SMTemp8温度1'], ['SMTemp8 Temp2', 'SMTemp8温度2'], ['SMTemp8 Temp3', 'SMTemp8温度3'], ['SMTemp8 Temp4', 'SMTemp8温度4'], ['SMTemp8 Temp5', 'SMTemp8温度5'], ['SMTemp8 Temp6', 'SMTemp8温度6'], ['SMTemp8 Temp7', 'SMTemp8温度7'], ['SMTemp8 Temp8', 'SMTemp8温度8']] | Yes (POST web_cgi_control.cgi)
134 | /var/datas/data.setting.html | HYBRID.list | Hybrid Mode | 1 | 2 | 196 | 1:2:196 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Only Diesel Mode', '单油机模式'], ['Diesel with AC Mode', '油机+市电模式']] | Yes (POST web_cgi_control.cgi)
135 | /var/datas/data.setting.html | HYBRID.list | Cyclic BC Interval | 1 | 2 | 124 | 1:2:124 | 3 | 14 | 14 | days | Yes (POST web_cgi_control.cgi)
136 | /var/datas/data.setting.html | HYBRID.list | Cyclic BC Start Time | 1 | 2 | 125 | 1:2:125 | 5 | 1 | 1 | [['0:00', '0:00'], ['1:00', '1:00'], ['2:00', '2:00'], ['3:00', '3:00'], ['4:00', '4:00'], ['5:00', '5:00'], ['6:00', '6:00'], ['7:00', '7:00'], ['8:00', '8:00'], ['9:00', '9:00'], ['10:00', '10:00'], ['11:00', '11:00'], ['12:00', '12:00'], ['13:00', '13:00'], ['14:00', '14:00'], ['15:00', '15:00'], ['16:00', '16:00'], ['17:00', '17:00'], ['18:00', '18:00'], ['19:00', '19:00'], ['20:00', '20:00'], ['21:00', '21:00'], ['22:00', '22:00'], ['23:00', '23:00']] | Yes (POST web_cgi_control.cgi)
137 | /var/datas/data.setting.html | HYBRID.list | Cyclic BC End Time | 1 | 2 | 126 | 1:2:126 | 5 | 7 | 7 | [['0:00', '0:00'], ['1:00', '1:00'], ['2:00', '2:00'], ['3:00', '3:00'], ['4:00', '4:00'], ['5:00', '5:00'], ['6:00', '6:00'], ['7:00', '7:00'], ['8:00', '8:00'], ['9:00', '9:00'], ['10:00', '10:00'], ['11:00', '11:00'], ['12:00', '12:00'], ['13:00', '13:00'], ['14:00', '14:00'], ['15:00', '15:00'], ['16:00', '16:00'], ['17:00', '17:00'], ['18:00', '18:00'], ['19:00', '19:00'], ['20:00', '20:00'], ['21:00', '21:00'], ['22:00', '22:00'], ['23:00', '23:00']] | Yes (POST web_cgi_control.cgi)
138 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 1 | 1 | 1 | 13 | 1:1:13 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
139 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 2 | 1 | 1 | 14 | 1:1:14 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
140 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 3 | 1 | 1 | 15 | 1:1:15 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
141 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 4 | 1 | 1 | 16 | 1:1:16 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
142 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 5 | 1 | 1 | 17 | 1:1:17 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
143 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 6 | 1 | 1 | 18 | 1:1:18 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
144 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 7 | 1 | 1 | 19 | 1:1:19 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
145 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 8 | 1 | 1 | 20 | 1:1:20 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
146 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 14 | 1 | 1 | 22 | 1:1:22 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
147 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 15 | 1 | 1 | 23 | 1:1:23 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
148 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 16 | 1 | 1 | 24 | 1:1:24 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
149 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Output 17 | 1 | 1 | 25 | 1:1:25 | 5 | 0 | 0 | [['Open', '断开'], ['Closed', '闭合']] | Yes (POST web_cgi_control.cgi)
150 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Clear Maintenance Run Time | 1 | 1 | 9 | 1:1:9 | 5 | 1 | 1 | [['Yes', '是']] | Yes (POST web_cgi_control.cgi)
151 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Manual Mode Time Limit | 1 | 2 | 184 | 1:2:184 | 3 | 0 | 0 | h | Yes (POST web_cgi_control.cgi)
152 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Maintenance Cycle Time | 1 | 2 | 11 | 1:2:11 | 3 | 7200 | 7200 | d | Yes (POST web_cgi_control.cgi)
153 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Slave Current Limit Value | 1 | 2 | 13 | 1:2:13 | 2 | 60 | 60 | % | Yes (POST web_cgi_control.cgi)
154 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Delta Voltage | 1 | 2 | 14 | 1:2:14 | 2 | 0.5 | 0.5 | V | Yes (POST web_cgi_control.cgi)
155 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Over Load Alarm Point | 1 | 2 | 34 | 1:2:34 | 3 | 70 | 70 | % | Yes (POST web_cgi_control.cgi)
156 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Imbalance Protection | 1 | 2 | 36 | 1:2:36 | 5 | 1 | 1 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
157 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Reporting | 1 | 2 | 48 | 1:2:48 | 5 | 1 | 1 | [['Fixed', '固定'], ['User Defined', '用户自定义']] | Yes (POST web_cgi_control.cgi)
158 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Lower Consumption | 1 | 2 | 9 | 1:2:9 | 5 | 0 | 0 | [['Disabled', '不使能'], ['Enabled', '使能']] | Yes (POST web_cgi_control.cgi)
159 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Power Peak Savings | 1 | 2 | 10 | 1:2:10 | 5 | 0 | 0 | [['Disabled', '不使能'], ['Enabled', '使能']] | Yes (POST web_cgi_control.cgi)
160 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | MPCL Pwr Range | 1 | 2 | 18 | 1:2:18 | 2 | 2.00 | 2.00 | kW | Yes (POST web_cgi_control.cgi)
161 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | MPCL Battery Discharge On | 1 | 2 | 19 | 1:2:19 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
162 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | MPCL Diesel Control On | 1 | 2 | 20 | 1:2:20 | 5 | 0 | 0 | [['Disabled', '不使能'], ['Enabled', '使能']] | Yes (POST web_cgi_control.cgi)
163 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Fail Safe Mode | 1 | 2 | 195 | 1:2:195 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Enabled', '使能']] | Yes (POST web_cgi_control.cgi)
164 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | PowerSplit Contactor Mode | 1 | 2 | 207 | 1:2:207 | 5 | 0 | 0 | [['Master Controlled', '主机控制'], ['Slave Controlled', '从机控制']] | Yes (POST web_cgi_control.cgi)
165 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI1 Alarm State | 1 | 2 | 211 | 1:2:211 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
166 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI2 Alarm State | 1 | 2 | 212 | 1:2:212 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
167 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI3 Alarm State | 1 | 2 | 213 | 1:2:213 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
168 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI4 Alarm State | 1 | 2 | 214 | 1:2:214 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
169 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI5 Alarm State | 1 | 2 | 215 | 1:2:215 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
170 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI6 Alarm State | 1 | 2 | 216 | 1:2:216 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
171 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI7 Alarm State | 1 | 2 | 217 | 1:2:217 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
172 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI8 Alarm State | 1 | 2 | 218 | 1:2:218 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
173 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI9 Alarm State | 1 | 2 | 473 | 1:2:473 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
174 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI10 Alarm State | 1 | 2 | 474 | 1:2:474 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
175 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI11 Alarm State | 1 | 2 | 475 | 1:2:475 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
176 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | DI12 Alarm State | 1 | 2 | 476 | 1:2:476 | 5 | 1 | 1 | [['Low', '低电平'], ['High', '高电平']] | Yes (POST web_cgi_control.cgi)
177 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Auto Mode | 1 | 2 | 42 | 1:2:42 | 5 | 1 | 1 | [['EMEA', '欧洲'], ['Normal', '普通']] | Yes (POST web_cgi_control.cgi)
178 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Test | 1 | 2 | 222 | 1:2:222 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Manual', '手动模式'], ['Automatic', '自动模式']] | Yes (POST web_cgi_control.cgi)
179 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Relay Test Time | 1 | 2 | 223 | 1:2:223 | 3 | 45 | 45 | s | Yes (POST web_cgi_control.cgi)
180 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | System Temp1 High 2 | 1 | 2 | 231 | 1:2:231 | 2 | 60 | 60 | deg.C | Yes (POST web_cgi_control.cgi)
181 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | System Temp1 High 1 | 1 | 2 | 232 | 1:2:232 | 2 | 50 | 50 | deg.C | Yes (POST web_cgi_control.cgi)
182 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | System Temp1 Low | 1 | 2 | 233 | 1:2:233 | 2 | -10 | -10 | deg.C | Yes (POST web_cgi_control.cgi)
183 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | High Load Level1 | 1 | 2 | 444 | 1:2:444 | 2 | 70 | 70 | % | Yes (POST web_cgi_control.cgi)
184 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | High Load Level2 | 1 | 2 | 445 | 1:2:445 | 2 | 85 | 85 | % | Yes (POST web_cgi_control.cgi)
185 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Solar Mode | 1 | 2 | 446 | 1:2:446 | 5 | 0 | 0 | [['Disabled', '禁止'], ['RECT-SOLAR', '模块太阳能混合'], ['SOLAR', '纯太阳能']] | Yes (POST web_cgi_control.cgi)
186 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Adjust Bus Input Voltage | 1 | 2 | 449 | 1:2:449 | 2 | 48.00 | 48.00 | V | Yes (POST web_cgi_control.cgi)
187 | /var/datas/data.sys_setting.html | PowerSystem.SYSTEM_GROUP.Power System,电源系统.list | Time Display Format | 1 | 2 | 456 | 1:2:456 | 5 | 0 | 0 | [['EMEA', '欧洲制式'], ['NA', '北美制式'], ['CN', '中国制式']] | Yes (POST web_cgi_control.cgi)
188 | /var/datas/data.sys_setting.html | PowerSystem.AC_UNIT.Rectifier AC,模块交流.list | Nominal Phase Voltage | 104 | 2 | 2 | 104:2:2 | 3 | 220 | 220 | V | Yes (POST web_cgi_control.cgi)
189 | /var/datas/data.sys_setting.html | PowerSystem.AC_UNIT.Rectifier AC,模块交流.list | Mains Failure Alarm Limit 1 | 104 | 2 | 4 | 104:2:4 | 2 | 15.0 | 15.0 | % | Yes (POST web_cgi_control.cgi)
190 | /var/datas/data.sys_setting.html | PowerSystem.AC_UNIT.Rectifier AC,模块交流.list | Mains Failure Alarm Limit 2 | 104 | 2 | 5 | 104:2:5 | 2 | 15.0 | 15.0 | % | Yes (POST web_cgi_control.cgi)
191 | /var/datas/data.sys_setting.html | PowerSystem.DC_UNIT.DC,直流.list | Shunt Current | 176 | 2 | 1 | 176:2:1 | 2 | 500.0 | 500.0 | A | Yes (POST web_cgi_control.cgi)
192 | /var/datas/data.sys_setting.html | PowerSystem.DC_UNIT.DC,直流.list | Shunt Voltage | 176 | 2 | 2 | 176:2:2 | 2 | 75.0 | 75.0 | mV | Yes (POST web_cgi_control.cgi)
193 | /var/datas/data.sys_setting.html | PowerSystem.DC_UNIT.DC,直流.list | Load Shunt Exist | 176 | 2 | 3 | 176:2:3 | 5 | 0 | 0 | [['No', '否'], ['Yes', '是']] | Yes (POST web_cgi_control.cgi)
194 | /var/datas/data.sys_setting.html | PowerSystem.LVD_GROUP.LVD Group,LVD组.list | HTD Reconnect Point | 186 | 2 | 61 | 186:2:61 | 2 | 38.0 | 38.0 | deg.C | Yes (POST web_cgi_control.cgi)
195 | /var/datas/data.sys_setting.html | PowerSystem.LVD_GROUP.LVD Group,LVD组.list | HTD Point | 186 | 2 | 60 | 186:2:60 | 2 | 40.0 | 40.0 | deg.C | Yes (POST web_cgi_control.cgi)
196 | /var/datas/data.sys_setting.html | PowerSystem.LVD_GROUP.LVD Group,LVD组.list | AC Fail Required | 186 | 2 | 59 | 186:2:59 | 5 | 1 | 1 | [['Disabled', '否'], ['Enabled', '是']] | Yes (POST web_cgi_control.cgi)
197 | /var/datas/data.sys_setting.html | PowerSystem.LVD_GROUP.LVD Group,LVD组.list | LVD 3 Enable | 186 | 2 | 64 | 186:2:64 | 5 | 0 | 0 | [['Disabled', '禁止'], ['Enabled', '允许']] | Yes (POST web_cgi_control.cgi)
198 | /var/datas/data.sys_setting.html | PowerSystem.FUEL_GROUP.Fuel Tank Group,油箱组.list | Fuel Number | 700 | 2 | 1 | 700:2:1 | 5 | 0 | 0 | [['0', '0'], ['1', '1'], ['2', '2'], ['3', '3'], ['4', '4'], ['5', '5']] | Yes (POST web_cgi_control.cgi)
199 | /var/datas/data.sys_setting.html | PowerSystem.FUEL_GROUP.Fuel Tank Group,油箱组.list | OB Fuel Number | 700 | 2 | 2 | 700:2:2 | 5 | 0 | 0 | [['0', '0'], ['1', '1'], ['2', '2']] | Yes (POST web_cgi_control.cgi)
200 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt1 Set As | 197 | 2 | 16 | 197:2:16 | 5 | 0 | 0 | [['Not Used', '不使用'], ['General', '通用'], ['Load', '负载'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
201 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt2 Set As | 197 | 2 | 17 | 197:2:17 | 5 | 0 | 0 | [['Not Used', '不使用'], ['General', '通用'], ['Load', '负载'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
202 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt3 Set As | 197 | 2 | 18 | 197:2:18 | 5 | 0 | 0 | [['Not Used', '不使用'], ['General', '通用'], ['Load', '负载'], ['Battery', '电池']] | Yes (POST web_cgi_control.cgi)
203 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt 1 Full Current | 197 | 2 | 1 | 197:2:1 | 2 | 500.0 | 500.0 | A | Yes (POST web_cgi_control.cgi)
204 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt 1 Full Voltage | 197 | 2 | 2 | 197:2:2 | 2 | 75.0 | 75.0 | mV | Yes (POST web_cgi_control.cgi)
205 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt 2 Full Current | 197 | 2 | 3 | 197:2:3 | 2 | 500.0 | 500.0 | A | Yes (POST web_cgi_control.cgi)
206 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt 2 Full Voltage | 197 | 2 | 4 | 197:2:4 | 2 | 75.0 | 75.0 | mV | Yes (POST web_cgi_control.cgi)
207 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt 3 Full Current | 197 | 2 | 5 | 197:2:5 | 2 | 500.0 | 500.0 | A | Yes (POST web_cgi_control.cgi)
208 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Shunt 3 Full Voltage | 197 | 2 | 6 | 197:2:6 | 2 | 75.0 | 75.0 | mV | Yes (POST web_cgi_control.cgi)
209 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Voltage Type | 197 | 2 | 9 | 197:2:9 | 5 | 3 | 3 | [['48 (Block4)', '48(Block4)'], ['Mid Point', 'Mid point'], ['24 (Block2)', '24(Block2)'], ['Disabled', '不允许']] | Yes (POST web_cgi_control.cgi)
210 | /var/datas/data.sys_setting.html | PowerSystem.EIB_UNIT.EIB 1,EIB1.list | Block In-Use Num | 197 | 2 | 12 | 197:2:12 | 3 | 8 | 8 |  | Yes (POST web_cgi_control.cgi)
211 | /var/datas/data.sys_setting.html | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | LVD 1 Control | 187 | 1 | 1 | 187:1:1 | 5 | 0 | 0 | [['Connected', '连接'], ['Disconnected', '断开']] | Yes (POST web_cgi_control.cgi)
212 | /var/datas/data.sys_setting.html | PowerSystem.OBLVD_UNIT.LVD Unit,LVD单元.list | LVD 2 Control | 187 | 1 | 2 | 187:1:2 | 5 | 0 | 0 | [['Connected', '连接'], ['Disconnected', '断开']] | Yes (POST web_cgi_control.cgi)
213 | /var/datas/data.sys_setting.html | PowerSystem.OBBATTFUSE_UNIT.Battery Fuse Unit,电池熔丝.list | Number of Battery Fuses | 159 | 2 | 1 | 159:2:1 | 5 | 2 | 2 | [['0', '0'], ['1', '1'], ['2', '2'], ['3', '3'], ['4', '4'], ['5', '5'], ['6', '6']] | Yes (POST web_cgi_control.cgi)
214 | /var/datas/data.udef_setting.html | UDEF_SET_1.list | EStop/EShutdown | 1 | 2 | 49 | 1:2:49 | 5 | 0 | 0 | [['Disabled', '禁止'], ['EStop', 'EStop'], ['EShutdown', 'EShutdown']] | Yes (POST web_cgi_control.cgi)